CENTRAL BOARD OF SECONDARY EDUCATION

Sector-5, Punchkula – 134109

Haryana

TENDER NOTICE

Sealed tenders under Two-Bid System are invited from reputed agencies which must have executed minimum two similar works each costing Rs. 6.00 lakh or more in reputed organization during the last two years.

1. Name of work       :           P.I.& C of CCTV System at RO Bldg., Panchkula.

2. Estimated Cost      :          Rs.7.50 lakh

3. EMD                     :           Rs.20000/-payable in f/o the Secretary, CBSE through

DD/BD

4. Cost of  Tender     :           Rs.500/- (Non-refundable)

5. Sale of Tender       :           upto 23.10.2009 from CBSE Regional Office, Sector-5,

Panchkula – 134109, Haryana

6. Last date for

submission of Tenders :      26.10.2009 upto 2:00 p.m.

7. Opening of Tech.-Bids   :  26.10.2009 at 2:30 p.m.

Tender can also be down-loaded through the Board’s website www.cbse.nic.in .  In case of down-loading Rs. 500/-in cash shall have to be deposited in the Regional Office as cost of the tender-form  &  receipt  enclosed with the Technical-Bid.  EMD must be placed in the Technical-Bid envelop.  Technical-Bid & Price-Bid envelopes be sealed separately & then placed in a bigger envelope superscribed  “CCTV Work”.  The tender should be dropped in the tender box placed at Reception Counter, Regional Office Bldg., Panchkula-134109.  The tender can also be sent through mail/registered post but must reach timely.  Incomplete & conditional tenders shall be summarily rejected.  The  Secretary, CBSE reserves the right to reject any or all the tenders without assigning any reason thereof.

Regional Officer

CENTRAL BOARD OF SECONDARY EDUCATION

Sector-5, Punchkula – 134109

Haryana

INSTRUCTIONS OF THE TENDERERS

- Incomplete and conditional tenders shall be summarily rejected.

- Rates are to be quoted in words and figures without any cutting/overwriting.

- The Short-Listed/Pre-qualified agencies shall be required to give demonstration/presentation of the equipment with proposed system.  In case the agency fails to report for demonstration of the system, it shall stand  disqualified.

- The agency should quote the rates, only after visiting the site and proper assessment of work.

- Complete brochure be attached with the Tech.-Bid.

- The Tech.-Bid shall be opened on 26.10.2009 at 2:30  pm in the presence of the tenderers.

- Any additional information required by CBSE in respect of the work experience shall be submitted by the tenderers within three days, failing which the offer shall not be entertained.

- Tenders received without EMD of Rs. 20000/- in the form of a Demand Draft shall be summarily rejected.

- In case of Down-loading the tender through the website,  the agency shall have to

deposit Rs. 500/- as cost of tender form in the CBSE Regional Office, Sector-5, Panchkula-134109, Haryana & enclose the receipt.

CENTRAL BOARD OF SECONDARY EDUCATION

Sector-5, Punchkula – 134109

Haryana

Tender form No…………………

Last date of submission: 26.10.2009

Upto 2:00 p.m.

Note :                                                : Tender must read the Instructions

Instructions to the Tenderers             : before filling the particulars in this part.

1. Credentials of the Tenderers

  - Name of the Agency with      ………………………………………………

Regn. No.                              ……………………………………………….

  - Office Address and                ………………………………………………

Tel. No.                                  ………………………………………………

  - Name(s) of the Proprieter/      ………………………………………………

Partners                                   ………………………………………………

1.4  WCT No.                                ………………………………………………

1.5  PAN No.                                 ………………………………………………

(with documentary evidence)

  - Annual turnover during last three years

(2005-06,2006-07,2007-08)      ………………………………………………

supported with documentary evidence………………………………………

2. Past Experience (preferable last three years)………………………………..

With all necessary documentary evidence………………………………

Such as copy of work order etc.

| SL. Nos. | Year | Name of the Organization | Cost of the work (executed) | Officers Concd. In the Organization with T.No. | Period From |
| --- | --- | --- | --- | --- | --- |
| 01. | 2006-2007 |  |  |  |  |
| 02. | 2007-2008 |  |  |  |  |
| 03. | 2008-2009 |  |  |  |  |

  - Has the firm been ever debarred/Black               …………………………………….

Listed by any organization ?                               ………………………………………

If ‘Yes’ the details thereof.                                 ………………………………………

  - The organizational set-up including

Technical infrastructure/staff strength

in all the categories.                                            ………………………………………

  - Similar work in hand at Panchkula/

Chandigarh and near- by cities                         ………………………………………

  - Particulars of Demand Draft paid as Earnest

Money :                                                                ……………………………………

Amount   : ………………………………

DD NO. :  ………………………………

Issuing Bank with date of issue  : …………………………………………………..

(Signature of the tenderer)

With complete address and seal

Tel. No.  :………………………………..

Mobile No.: …………………………….

Place  :   ………………………………..

Date  :     ……………………………….

Technical specification

- Dome/Box CCTV Camera

Type	Very High Resolution Day & Night Camera

Sensor 	1/3” CCD (Sony Supper HAD CCD Sensor)			Signal System	540TV lines or better

Video Output	1-Vp-p/75Ω

Sensitivity	0.1 Lux (F 1.2) or better

S/N Ratio	48db or better

Power 	12V±10% (for rough power conditions)

Lens	3mm-8mm, fixed focal, Auto iris,

Iris Drive	DC (Must have the IRIS Control for different light condition)

Day & Night	Auto/manual,

Back Light Compensation	Auto/manual,

White Balance	Auto/manual,

If Box Camera is quoted it should be quoted with suitable housing and stand for indoor application

Acceptable brands

Samsung, Pelco, Honeywell, Bosch, Panasonic, GE.

- Scanner

Pan Angle 	upto 340 deg, but not less than 290 deg.

Pan control 	External Adjustment

Power Source 	AC 220 V±10% (60/50HZ) AC

Power Consumption Pan: 	≤ 5W

Load Rating Pan 	≥ 5 kg

Note

Scanner should not be quoted with above cameras. It should be quoted independently.

3.	Outdoor Speed Dome Camera

Type                                        	Very High Resolution Day & Night Speed

Dome camera

Sensor 	1/3” or 1/4” Interline CCD, WDR camera

Signal System	520TV lines or better

Optical Zoom	30X (3mm to 90mm or more)

Digital Zoom	10X or more

Protocol support 	PELCO-D, Panasonic, Vicon, Honeywell,

(Multiple protocol)

Wide Dynamic Range	52db

Video Output	1-Vp-p/75Ω

Light Sensitivity	0.00001 lx or better (Camera with lux value

0.00005 or higher are not acceptable e;g:

0.01 lux, 0.05 lux, 0.1 lux etc., as the

Application is outside area.)

Motion Detection	On / Off selectable

Preset Positions	200 or more

Rotation Angle	Pan : 360° , Tilt : -0° ~ -180°

Focus Control	Auto / Manual

Communication	RS-485, RS-422, RS-232C, TCP/IP

Operating Temperature	0°C ~ +50°C

Day & Night	Auto/manual, User Selectable

Back Light Compensation	Auto/manual, User Selectable

White Balance	Auto/manual, Use Selectable

Power Supply 	Included

Housing and Bracket 	Outdoor housing with wall/pole mount

bracket and cable Management

Note: Separate PAN, TILT and Zoom camera configuration is not acceptable, hence

should not be quoted.

Acceptable brands

Honeywell, Panasonic, Samsung, Pelco, Bosch, GE.

4.	Indoor Speed Dome Camera

Type 	Very High Resolution Day & Night Speed

Dome Camera

Sensor 	1/3” or 1/4" Interline CCD, WDR Camera

Signal System 	520 TV lines or better

Optical Zoom 	10X (3mm to 30mm or more)

Digital Zoom	10X or more

Protocol support 	PELCO-D, Panasonic, Vicon, Honeywell,

(Multiple protocol)

Video Output	1-Vp-p/75 Ω

Sensitivity 	0.1 Lux

Motion Detection 	On / Off selectable

Preset Positions 	128 or more

Rotation Angle 	Pan : 300° or more, Tilt : -0° ~ -180°

Focus Control	Auto / Manual

Communication 	RS-485, RS-422, RS-232C, TCP/IP

Operating Temperature 	0° ~ +50°C

Day & Night 	Auto/manual, User Selectable

Back Light Compensation	Auto/manual, User Selectable

White Balance 	Auto/manual, user Selectable

Power Supply 	Included

Housing and Bracket 	Indoor housing with bracket and cable

Management

Note:  Separate PAN, TILT and Zoom Camera configuration is not acceptable, hence

should not be quoted.

Acceptable brands

Honeywell, Panasonic, Samsung, Pelco, Bosch, GE.

- Digital Video Recorder

Video input	16 channels

Video output				BNC/RCA/VGA

Compression 	H.264

Resolution 	352X288 to 704X576 (PAL), should be

selectable.

Display Rate	Min 400 fps (PAL),

Recording rate	Min 400 fps (PAL),

Recording bit rate  	variable upto 1Mps

Recording mode	Manual/scheduled

Hard disk capacity 	1000G inbuilt,

Expandability 	Provision for additional hard disks to be inbuilt, upto 3TB Backup 	DVD R/W/ and USB, Remote.

Communication	TCP/IP,  RS-485, RS-232

Remote operation  	TCP/IP, inbuilt web server, Remote

software included.

Operating Temperature	0 deg to 50 deg

Power 	230VAC

Acceptable brands

Samsung, Honeywell, Hikivision, Penasonic, Pelco, GE,

- Speed Dome Keyboard/Controller

Type 					LCD keyboard

PTZ Control				3 Axis.

Auto surveillance			Tour, group, Swing, preset. Etc.

Communication 				RS-485/RS232/TCP/IP

Protocol 					Pelco-D, Panasonic, Samsung, Honeywell

Acceptable brands

Samsung, Honeywell, Panasonic, Pelco, GE,

Note:  Before quoting, Please ensure that above Keypad/Controller should be able to control the DVR and Speed Dome Camera. As DVR may not be placed in same room, therefore it operation should be accessible from the Keyboard anywhere in the premises

- Monitor

Type	LCD

Size	21 inches or more

Contrast Ratio	5,000:1 or better

Brightness 	min 300cd/m2

View Angle 	160H/V or more

Resolution 	1680 X 1050

Response Time 	5 ms or less

Stand 	Wall mount or table top, included

Power 	230V AC

Acceptable brands

Samsung, Honeywell, LG, SONY, PANASONIC.

- Monitor

Type	LCD

Size	32 inches or more

Contrast Ratio	5,000:1 or better

Brightness 	min 300cd/m2

View Angle 	170H/V or more

Resolution 	1680 X 1050

Response Time 	5 ms or less

Stand 	Wall mount & table top, included

Power 	230V AC

Acceptable brands

Samsung, Honeywell, LG, SONY, PANASONIC.

- Video Switcher

Video input	16 Channel

Video input type 	Composite/ RCA/BNC

Remote Expansion panels 	4 Nos with Local IR remote control

Switching 	Auto/manual, selectable

- Line interactive UPS

Capacity 	IKV

Switching time 	≤ 10ms

Input Voltage 	160-270V AC

Output Voltage 	230V± 10%

- Power Supply

Type 	SMPS

Input	230V± 10%

Output 	12± 10%

Amp Rating 	3 Amp

Switching time 	≤ 10ms

- Cables

12. (a) Video cable 				RG-59

12. (b)  Power cable 				2 core 1.5 sqmm, multi strand

12. (c) Data cable 				8 core data cable, 14/38

Acceptable Brands

Finolex, Deltron, Excel, Incol, Plaza, D-Link,

- Conduit & Channels

(a) Conduit/channel 			1” PVC Conduit

Acceptable makes

Plaza, Excel, AKG, or ISI marked

Note: Before quoting for, please ensure from your end that all these devices should are compatible with each other, as there are multiple protocols for different manufactures. CBSE will not be responsible in any way/whatsoever reason.

Compliance Statement

| S.No. | Requirement (Description/Statement) | Compliance Deviation 0% (+/-) | Model & Make |  | Description of Model & Make being offered |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Make | Model |  |

1								Dome CCTV Camera/Box camera

|  | Type: Very High Resolution Day & Night Camera |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Sensor: 1/3” CCD (Sony Supper HAD CCD Sensor) Signal System: 530TV lines or better Video Output: 1-Vp-p/75 Sensitivity: 0.1 Lux (F 1.2) or better S/N Ratio: 48db or better Power: 12V±10% (for rough power conditions) Lens: 3mm-8mm, fixed focal, Auto iris, Iris: Drive DC (Must have the IRIS Control for different light condition) Day & Night: Auto/manual, Flicker less: on/off (user selectable, DIP switches or VR setting) |  |  |  |  |

2										Scanner

|  | Pan Angle: upto 340 deg, but not less than 290 deg. Pan control: External Adjustment Power Source: AC 220 V±10% (60/50HZ) AC Power Consumption Pan: ≤ 5W Load Rating Pan ≥ 5 kg |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

3								Outdoor Speed Dome Camera

|  | Type: Very High Resolution Day & Night Speed Dome camera Sensor: 1/3" or 1/4" Interline CCD, WDR camera Signal System: 530TV lines or better Optical Zoom: 35X or more Digital Zoom: 10X or more Protocol Support: PELCO-D, Panasonic, Vicon, Honeywell, Wide Dynamic Range: 52db Video Output: 1-Vp-p/75 Light Sensitivity: 0.00001 1x or better (camera with lux value 0.0005 or higher are not acceptable e;g: 0.01 lux, 0.05 lux, 0.1lux etc., as the application is outside area.) Motion Detection: On / Off selectable Preset Positions: 200 or more Rotation Angle Pan: 360º , Tilt : -0º ~ -180º Focus Control: Auto / Manual Communication: RS-485, RS-422, RS-232C, TCP/IP Operating Temperature: 0ºC ~ +50ºC Day & Night: Auto/manual User Selectable Back Light Compensation: Auto/manual, User Selectable White Balance: Auto/manual, Use Selectable Power Supply: Included Housing and Bracket: Outdoor housing with wall/pole mount bracket and Cable management |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

4								Indoor Speed Dome Camera

|  | Type: Very High Resolution Day & Night Speed Dome camera Sensor: 1/3" or 1/4" Interline CCD, WDR camera Signal System: 520TV lines or better Optical Zoom: 10X (3mm to 30 mm or more) Digital Zoom: 10X or more Protocol Support: PELCO-D, Panasonic, Vicon, Honeywell, (Multiple Protocol) Video Output: 1-Vp-p/75 Sensitivity: 0.1 Lux Motion Detection: On / Off selectable Preset Positions: 128 or more Rotation Angle Pan: 300º or more, Tilt : -0º ~ -180º Focus Control Auto/Manual Communication: RS-485, RS-422, RS-232C, TCP/IP Operating Temperature: 0ºC ~ +50º C Day & Night: Auto/manual User Selectable Back Light Compensation: Auto/manual, User Selectable White Balance: Auto/manual, Use Selectable Power Supply: Included Housing and Bracket: Indoor housing with bracket and cable Management |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

5								Digital Video Recorder

|  | Video input: 16 channels Video output: BNC/RCA and VGA Compression: H.264/MPEG-4 Recording Resolution: 352x288 to 704x576 (PAL), should be selectable. Dual Streaming: Yes Display Rate: Min 400 fps (PAL) at CIF Recording rate: Min 400 fps (PAL) at CIF Image Quality: User Selectable Recording bit rate: variable upto 1Mps Recording mode: Manual/scheduled Hard disk capacity: 1000G inbuilt, Expandability: Provision for additional hard disks to be inbuilt, upto 4TB Backup DVD R/W/ and USB, Remote. Communication: TCP/IP, RS-485, RS-232 Remote operation: TCP/IP, inbuilt web server, Remote software included. Power: 230VAC |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

6								Speed Dome Keyboard/Controller

|  | Type: LCD keyboard, PTZ Control: 3 Axis. Auto surveillance: Tour, group, Swing, preset. Etc. Communication: RS-485/RS232/TCP/IP Protocol: Pelco-D, Panasonic, Samsung, Honeywell |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

7								Monitor-21 Inch

|  | Type: LCD Size: 21 inches or more Contrast Ratio: 5,000:1 or better Brightness: min 300cd/m2 View Angle: 160H/V or more Resolution 1680 X 1050 Response Time 5 ms or less Power 230 AC Stand Wall mount or table top, included |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

8								Monitor-32 Inch

|  | Type: LCD Size: 32 inches or more Contrast Ratio: 5,000:1 or better Brightness: min 300cd/m2 View Angle: 160H/V or more Resolution 1680 X 1050 Response Time 5 ms or less Power 230 AC |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

9								Video Switcher

|  | Video input: 16 Channel Video input type: Composite/ RCA/BNC Remote Expansion panels: 4 Nos with Local IR remote control Switching Time: Auto/manual, selectable |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

10								Line interactive UPS

|  | Capacity 1KV Switching time ≤ 10ms Input Voltage 160-270V AC Output Voltage 230V± 10% |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

11								Power Supply

|  | Type SMPS Input 230± 10% Output 12± 10% Amp Rating 3 Amp Switching time ≤ 10ms |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

12								Cables

|  | 9. (a) Video cable RG-59U 9. (b) Power cable 2 core 1.5 sqmm, multi stand 9. (c) Data cable 8 core data cable, 14/38 |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

13								Conduit & Channels

|  | 10. (a) Conduit 1” PVC Conduit 10. (b) Channel 1” PVC Channel |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

Authorised Signatory

Name of organization

Name of auth. Person

Tel/Mob. No:

Email ID

Sign with Seal

Price Bid

Sl. No   Discription               Make          Model	       Qty	   Unit Price                    Amount

1.         Dome/Box C.C.T.V. Camera    	       15 No

2.        Scanner 	      Rate only

- Outdoor Speed Dome Camera   		       1 No

- Indoor Speed Dome Camera		      Rate only

- Digital Video Recorder    	       1 No

- Speed Dome Keyboard/Controller 	       1 No

- 21” LCD Monitor		      	       2 No

- 32” LCD Monitor 			       1 No

- 16 Channel Video Switcher		       1 No

- UPS    					       1 No

- Power Supply				       3 No

- Cable

(i)  Video Cable 				    1000 R mtrs.

(ii) Power cable 				      500 R mtrs.

13.       PVC Conduit/channel     	  	     800 R mtrs.

14.      Installation & Commissioning charges

(Including necessary junction boxes,

Termination boxes, Connectors, accessories,

Saddle & spacer etc, including training

to CBSE staff/ in charge person about

Operation of the system      					     LS

15.     AMC for 5 Years (non Comprehensive)				     LS

All above should be inclusive of all kinds of tax, packing forwarding etc.

Terms and Conditions

- The work must be executed as per the specifications and best Engineering practice.

- Rates must be quoted both in figures & words.

- Cutting/overwriting should be avoided.  In case of any cutting/overwriting, the same must be initialed/authenticated.

- Rates are to be quoted on the prescribed format.

- CBSE reserves the right to deviate the quantity.  Any item can be deleted if not required as per site condition. Payment shall be made on the basis of the measurements.

- ALL T & P shall be arranged by the agency at their own cost.

- In case of any damage to the structure, the same shall be made good by the agency.

- The rates quoted must be inclusive of all Taxes.

- Since the firms are required to give demonstration of the proposed system, Board does not bind itself to accept the Lower-bid or to give any reasons for its decisions.

- The agency shall be bound to complete the work within 430 days from the issue of the work order.

- In case of delayed execution a penalty @ 1% per week shall be levied.

- The agency selected for the work shall deposit a performance guarantee equivalent to 10% of the total value of the work. It can be submitted in the form of the Bank Guarantee.

- In case of slow progress & the Board put to any financial loss, the CBSE shall invoke the Bank Guarantee.

- The agency shall submit all the guarantee cards/Brochures to the Engineer-In-Charge.

- All materials brought to site shall be subjected to the approval of the Engineer-In-Charge.  In case of any unapproved material is used, the same shall be removed by the agency at his own expense.

- Comprehensive AMC shall for a period of 5 years shall have to be undertaken by the agency for which separate agreement shall be executed.

- 10% of the basic value of bill shall be retained as defect liability for a period of six months effective from the date of completion.  In case of satisfactory performance, the same shall be refunded without interest.

- No running payment is permissible however, the final bill would be processed & cleared within 15 days from the date of its submission.

- The equipments /products installed must be guaranteed for a period of one year from the date of completion.

- The safety & security of the equipments/products after its installation shall rest with the Board.

- The complaint if reported shall be got rectified by the agency within 24 hours failing which a penalty @ Rs. 200/- per day shall be levied.

- In case of any dispute, the Chairman shall have the right to appoint an Arbitrator whose decision shall be final & binding on both the parties.

( Signature of the Agency)

With complete address and seal

Add.__________________

____________________

Tel. No.:__________________

Mobile No.:________________